Provide comprehensive WASH, Shelter/NFI, and Protection interventions to mitigate morbidity and mortality among children and their families in response to the Sudan crisis

Bid documents

North Kordofan State

Supply, installation and connection of 5 Plastic water tanks 5,000 Litter in Al-mena Al-pari “Land Port” IDPs camp in Shikan locality

Water Supply

January 2026

# Specifications & Performance Requirements

General Provisions

1-Scope and Applications

These Specifications supply, installation and connection 5 water tanks 5000L (Althoraya 3 layers) in land port IDPs camp, installation of tap stand in term of 4 taps for each tank, construction of small towers from red bricks and cement and printing of logos for the tanks, installation of metal signposts according to specifications bellow.

2- Requirements of Specifications, Standards and Brand Names

The supplier shall fulfil all requirements and obligations under all Clauses of the Specifications. Neither the following Clauses of this Specification, any descriptions therein nor the quantities shall limit the obligations of the Contractor under the Conditions of Contract. Where items are not included in the Bill of Quantities for any such requirements or obligations, the cost of such requirements or obligations shall be deemed to be spread over all the items of the Bill of Quantities. All Sudanese, or other Standards mentioned herein shall be deemed to form part of this Specification. All references to such standards shall be to the latest edition or revision thereof unless otherwise stated. Where a specific Sudanese or other Standard is referred to in this Specification, another Standard will be acceptable, provided that it ensures a quality of material and workmanship equal to or better than the Standard referred to. If the Contractor intends to use such alternative Standard, he shall notify the Sector coordinator thereof. submitting with his notice two (2) copies (in English or Arabic) of the proposed Standard and shall not order any material or perform any work unless and until he has obtained the Sector Coordinator's approval of such Standard. Brand names, where used in the Specification or on the drawings, are only intended to define a standard of quality and performance and the Contractor may use alternative products of at least equal quality and capacity. When the Contractor offers alternatives, the supplier shall submit to the Sector Coordinator for approval a statement detailing the alternatives, and shall include full technical descriptions, drawings and specifications, and shall provide such full information as is required to enable the Contractor to demonstrate to the Sector Coordinator that the alternative is equivalent to the item specified. The Contractor when called for shall produce any further information that the Sector Coordinator may require.

BOQ for supply, installation and connection 5 water tanks 5000L

| SL # | DESCRIPTION | QUANTITY | unit | UNIT PRICE SDG | TOTAL PRICE SDG |
| --- | --- | --- | --- | --- | --- |
| 1 | Mobilization to the site: Mobilization shall consist of preparatory work including, but not limited to, those necessary to the movement of personnel, equipment, supplies and incidentals to the project site in Al-mena Al-pari “Land Port” IDPs camp. ترحيل كل المواد والمعدات اللازمة لتنفيذ العمل بالإضافة للعمال والمهندسين إلى مواقع المشروع بمعسكر الميناء البري | 1 | Job |  |  |
| 2 | Supply 3 water tanks 5000L 3 layers vertical Althoraya brand توريد خزان مياه سعة 5000 لتر راسي ماركة الثريا 3 طبقات | 5 | PC |  |  |
| 3 | Printing the SOS Sahel logo and Doners on the tank. طباعة شعار المنظمة والمانح على الخزانات مقاس 100x 100 سم لكل شعار | 5 | tanks |  |  |
| 4 | Construction of towers according to technical specifications: - طول الحامل 1.20 متر، 40 سم داخل الأرض، 80 سم فوق سطح الأرض. - حفر قاعدة بعرض 40 سم وعمق 50 سم وأبعاد 250 × 250 سم. - عمل فرشة من الخرسانة المسلحة بسمك 10 ملم باستخدام خلطة خرسانية 1:2:4 مع تسليح شبكي باستخدام حديد قطر 12 بتوزيع 15 سم من الجانبين. - عمل قصة بطوبتين من الطوب الاحمر نمرة واحد بارتفاع 40 سم. - توريد ردميات ترابية 20 سم وردم ومندلة ورش غرف الحامل علي طبقتين. - توريد مواد وعمل المباني من الطوب الاحمر نمرة واحد بسمك طوبة ونص بارتفاع 50 سم بخلطة اسمنتية 1:6. - توريد وصب بلاطة الحامل وفق الابعاد بسمك 10 سم باستخدام الخرسانة المسلحة 1:2:4 مع حديد تسليح 12 مم بتوزيع 15 سم من الجانبين. - تثبيت الخزان البلاستيكي على القاعدة - استخراج خط من الخزان البلاستيكي لتوصيل الحنفيلت باستخدام مواسير ال PPR قطر 2 بوصة مع عمل بلف علي ان تكون التوصيلات داخل جدران الحامل. - تشيد سور من الطوب الاحمر والمونة الاسمنتية بارتفاع 30 سم علي اطراف الخزان مع الطلاء والبياض - تركيب عدد 4 حنفيات ستيل 1 بوصة ذات جودة عالية - تشييد مصرف للمياه الراجعة بطول 2.5 متر على ان تصب في بركة مياه يتم تشييدها من الطوب الاحمر والمونة الاسمنتية بابعاد 60 * 60 سم وعمق 30 سم مع البياض. - توريد مواد وعمل بياض لجميع الحوامل باستخدام مونة اسمنتية 1:8 مع الرش الجيد ثم الطلاء بالبوماستك. يتم تنفيذ المواصفات اعلاه وفقا لتوجيهات المهندس المشرف حسب الصورة المرفقة ادناه | 5 | towers |  |  |
| 5 | Supply and construction of 2-meter height fence made of galvanized steel chain-link wire (3 mm) fixed on 2 meter height (2.25 m of pipe should be above ground level and 0.5 m below ground level including the bending length), 2 inch steel pipe 2.8mm, spaced at 2 meters distances with skewer 3 Linya 12/6m (at top, bottom and the middle), the 2 inch steel pipes (posts) will be erected in a 40 * 40 * 60 cm plain concrete base, around the existing water station as 5*5 (19 m for water point). Steel pipe 3inch 2.8 mm should be fixed with two supported one meter steel pipe 2 inch 2.8mm at the four corners of the fence. توريد وتصنيع سياج بارتفاع 2 متر مصنوع من مواسير القلفنايز 2 بوصة 2.8مم وسلك الحظائر القلفنايز (بسمك 3 مم بفتحات أقصاها 5سم) المواسير مثبتة على إرتفاع2.25 متر فوق مستوى سطح الأرض متضمنة الطول المثني و0.5 متر تحت مستوى سطح الأرض ومتباعدة بمسافة 2 متر، مع عمل ثلاثة خطوط من السيخ 3 لينية 12مم بطول 6 أو 12 متر ملحومة على السور في الأعلى والوسط والاسفل. تثبت المواسير الحديدية 2 بوصة في قاعدة اسمنتية في حفرة بالأبعاد 40*40*60سم ويكون طول السياج 19 متر لكل نقطة مياه (5*5م مطروح منها مساحة الباب 1 متر). كما يجب تثبيت مواسير 3 بوصة 2.8 مم مدعومة بمواسير 2 بوصة 2.8مم بطول 1 متر على الجانبين لكل ماسورة في الاربعة أركان لكل سور. | 57 | ML |  |  |
| 6 | Construction of Single gate Single gate shall be manufactured from expended metal (decoration), lockable fixed on steel angle 1.5 inch 3mm which is welded to 3 inch thickness 2.8mm posts galvanized pipe. Single gate dimensions: 2-meter height 1-meter length other specifications will be according to the drawings or WASH coordinator advise تصنيع باب للسور الحديدي بضلفة واحدة حسب المواصفات أعلاه | 5 | PC |  |  |
| 7 | Manufacture and erect metal signpost made from steel blade sheet 3 mm thick and 140cm X80 cm welded and fixed to 2.5-meter length rectangular steel pipe 3cm X 6cm, 2 meter over ground level and 50 cm underground level and erected on concrete base 0.5X0.5X60cm all other details will be provided by the project. Including painting with green and white paint تصنيع وتثبيت لافتة تحمل تفاصيل المشروع حسب المواصفات أعلاه | 5 | Pc |  |  |
| TOtal AMOUNT OF TENDER |  |  |  |  |  |

الجدول الزمني لانجاز العمل :--------------------------------------------------------------------------